## Hoja1
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
-49.33 | 30%CO2+10%SF6+60%Ar | 51.13 | 233.82 | 11677.29 | 0.15 | 10.32 | 1800 | 9.64 | 1700
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700 |  |  | CO
13.44 | 90%CO2+10%NF3 | 43.49 | 296.59 | 7935.27 | 0.26 | 11.77 | 1000 | 9.78 | 800 |  |  | Argon
4.24 | 80%CO2+20%NF3 | 45.05 | 287.39 | 7851.58 | 0.25 | 11.7 | 1200 | 9.76 | 900 |  |  | N2
-5.46 | 70%CO2+30%NF3 | 46.21 | 277.69 | 7482.4 | 0.23 | 12.11 | 1100 | 9.82 | 850
-8.36 | 67%CO2+33%NF3 | 46.48 | 274.79 | 7231.16 | 0.22 | 10.68 | 1150 | 9.85 | 750
-14.97 | 60%CO2+40%NF3 | 47.45 | 268.18 | 6935.24 | 0.22 | 10.83 | 1140 | 10.97 | 700
-18.59 | 56%CO2+44%NF3 | 48.45 | 264.56 | 6695.28 | 0.22 | 10.79 | 1150 | 9.68 | 800
-28.52 | 44%CO2+56%NF3 | 50.36 | 254.63 | 5998.71 | 0.22 | 10.02 | 1150 | 9.69 | 800
-37.9 | 30%CO2+70%NF3 | 52.25 | 245.25 | 5348.84 | 0.22 | 9.71 | 1150 | 9.89 | 800
-42.94 | 20%CO2+80%NF3 | 53.55 | 240.21 | 5024.3 | 0.22 | 11.38 | 1100 | 9.11 | 1000
-52.02 | 47%CO2+10%NF3+43%Ar | 51.45 | 231.13 | 6104.49 | 0.27 | 10.22 | 700 | 9.78 | 700
-53.39 | 10%CO2+80%NF3+10%Ar | 54.45 | 229.76 | 4663.12 | 0.24 | 9.97 | 1150 | 10.63 | 1200
-29.15 | 100%NF3 | 47.22 | 254 | 7460.7 | 0.05 | 10.91 | 1800 | 9.85 | 400
-39.15 | 100%NF3 | 50.54 | 244 | 6060.7 | 0.14 | 10.52 | 1500 | 10.96 | 600
-49.15 | 100%NF3 | 54.07 | 234 | 4660.7 | 0.19 | 10.74 | 1150 | 10.57 | 700
-46.63 | 10%CO2+90%NF3 | 50.31 | 236.52 | 4804.19 | 0 | 0 | 0 | 9.95 | 914
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
12.77 | 90%CO2+10%CF4 | 43.55 | 295.92 | 7882.69 | 0.25 | 10.343 | 1100 | 10.48 | 700
2.86 | 80%CO2+20%CF4 | 45.09 | 286.01 | 7782.63 | 0.23 | 11.41 | 1200 | 10.51 | 775
-7.74 | 70%CO2+30%CF4 | 46.88 | 275.41 | 7399.22 | 0.2 | 10.51 | 1300 | 10.34 | 800
-18.39 | 60%CO2+40%CF4 | 48.97 | 264.76 | 6790.9 | 0.2 | 10.65 | 1350 | 9.2 | 850
-28.37 | 50%CO2+50%CF4 | 51.7 | 254.78 | 6072.33 | 0.24 | 9.81 | 1500 | 9.57 | 1250
-37.24 | 40%CO2+60%CF4 | 52.49 | 245.91 | 5376.98 | 0.2 | 9.91 | 1400 | 10.07 | 750
-44.73 | 30%CO2+70%CF4 | 53.5 | 238.42 | 4797.8 | 0.17 | 9.75 | 1350 | 10.31 | 550
-48.07 | 50%CO2+10%CF4+40%Ar | 51.42 | 235.08 | 6108.85 | 0.27 | 10.57 | 750 | 10.61 | 700
-40.32 | 20%CO2+80%CF4 | 53.69 | 242.83 | 4675.46 | 0.18 | 10.7 | 1600 | 11.29 | 800
-53.98 | 10%CO2+90%CF4 | 55.24 | 229.17 | 4121.62 | 0.14 | 10.25 | 1350 | 9.68 | 500
-35.64 | 100%CF4 | 50.73 | 247.51 | 6000 | 0.13 | 10.81 | 2550 | 9.41 | 1200
-45.64 | 100%CF4 | 53.4 | 237.51 | 5300 | 0.15 | 12.3 | 1960 | 9.96 | 1100
-55.64 | 100%CF4 | 56.97 | 227.51 | 3950 | 0.2 | 10.7 | 1600 | 9.59 | 1200
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
12.85 | 90%CO2+10%Kr | 42.72 | 296 | 7953.13 | 0.25 | 9.78 | 900 | 11.06 | 550
3.49 | 80%CO2+20%Kr | 43.73 | 286.64 | 7971.48 | 0.23 | 10.93 | 800 | 10.49 | 550
-6.37 | 70%CO2+30%Kr | 45.41 | 276.78 | 7806.3 | 0.24 | 10.06 | 750 | 9.99 | 600
-15.9 | 60%CO2+40%Kr | 47.12 | 267.25 | 7493.5 | 0.27 | 9.75 | 700 | 10.38 | 750
-24.55 | 50%CO2+50%Kr | 47.82 | 258.6 | 7237.87 | 0.25 | 9.95 | 600 | 10.13 | 550
-32.76 | 40%CO2+60%Kr | 48.07 | 250.39 | 7024.97 | 0.22 | 10.64 | 500 | 10.61 | 425
-39.92 | 30%CO2+70%Kr | 48.71 | 243.23 | 6908.85 | 0.22 | 10.89 | 450 | 10.09 | 425
-47.93 | 20%CO2+80%Kr | 49.03 | 235.22 | 6845.67 | 0.2 | 10.89 | 400 | 9.96 | 375
-48.63 | 30%CO2+40%Kr+30%Ar | 50.77 | 234.52 | 9291.4 | 0.25 | 9.92 | 800 | 11 | 800
-58.27 | 10%CO2+90%Kr | 49.88 | 224.88 | 6588.89 | 0.2 | 10.1 | 350 | 9.97 | 350
-73.67 | 100%Kr | 50.89 | 209.48 | 5725 | 0.15 | 10.21 | 250 | 9.93 | 250
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K) | Compressor Isoentropic Efficiency | 0.75
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700 | TIT (K) | 823.15
13.35 | 90%CO2+10%CH4 | 43.03 | 296.5 | 8281.61 | 0.26 | 10.97 | 1050 | 10.86 | 700 | TIP (kPa) | 25000
4.1 | 80%CO2+20%CH4 | 44.41 | 287.25 | 8766.79 | 0.24 | 9.97 | 1200 | 10.99 | 850 | Power Output (kW) | 10000
-6.16 | 70%CO2+30%CH4 | 45.25 | 276.99 | 8989.2 | 0.2 | 9.79 | 1300 | 10.18 | 700 | Turbine Isoentropic Efficiency | 0.9
-17.71 | 60%CO2+40%CH4 | 47.29 | 265.44 | 9055.31 | 0.2 | 10.69 | 1350 | 9.95 | 850
-30.5 | 50%CO2+50%CH4 | 50.53 | 252.65 | 8692.27 | 0.2 | 10.4 | 1200 | 11.5 | 800
-44.02 | 36%CO2+64%CH4 | 51.41 | 239.13 | 8027.37 | 0.2 | 11.71 | 1400 | 10.34 | 675
-56.97 | 30%CO2+70%CH4 | 53.94 | 226.18 | 7111.83 | 0.2 | 11.61 | 1100 | 10.17 | 525
-69.56 | 20%CO2+80%CH4 | 55.11 | 213.59 | 6335.04 | 0.15 | 10.26 | 950 | 10.88 | 350
-39.14 | 50%CO2+10%CH4+40%Ar | 49.81 | 244.01 | 12657.38 | 0.14 | 10.01 | 1700 | 10.41 | 2700
-81.7 | 10%CO2+90%CH4 | 57.9 | 201.45 | 5461.41 | 0.17 | 9.62 | 900 | 10.74 | 350
-92.59 | 100%CH4 | 61.09 | 190.56 | 4799.2 | 0.2
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
11.93 | 90%CO2+10%CO | 43.42 | 295.08 | 8704.47 | 0.28 | 10.71 | 1100 | 10.04 | 940
1.47 | 80%CO2+20%CO | 44.32 | 284.62 | 9749.27 | 0.25 | 12.24 | 1200 | 10 | 1150
-10.55 | 70%CO2+30%CO | 47.68 | 272.6 | 11233.98 | 0.21 | 10.64 | 1450 | 10.96 | 1700
-24.22 | 60%CO2+40%CO | 47.39 | 258.93 | 12328.27 | 0.18 | 11.12 | 1800 | 10.49 | 2200
-42.35 | 50%CO2+50%CO |  | 240.8 | 13641.63
-111.36 | 40%CO2+60%CO |  | 171.79 | 33145.83
-133.3 | 30%CO2+70%CO |  | 149.85 | 35320.03
-116.04 | 20%CO2+80%CO |  | 167.11 | 4270.66
-133.17 | 10%CO2+90%CO |  | 149.98 | 3882.33
-150.29 | 100%CO | 67.67 | 132.86 | 3694 | 0.2 | 10.87 | 375 | 10.48 | 325
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
12.13 | 90%CO2+10%N2 | 42.66 | 295.28 | 8958.59 | 0.25 | 11.44 | 1100 | 10.6 | 800
1.14 | 80%CO2+20%N2 | 43.97 | 284.29 | 10559.01 | 0.22 | 11.24 | 1400 | 9.96 | 1200
-10.44 | 67%CO2+33%N2 | 44.41 | 272.71 | 12347.67 | 0.18 | 11.14 | 2000 | 10.19 | 1200
-25.3 | 60%CO2+40%N2 |  | 257.85 | 14526.98 | 0.14 |  | 2400 |  | 1400
| 50%CO2+50%N2 |  | 234.74 | 17968.99
| 40%CO2+60%N2 |  | 219.68 | 43385
| 30%CO2+70%N2 |  | 199.01 | 205940
| 20%CO2+80%N2 |  | 177.41 | 407450
| 10%CO2+90%N2 |  | 153.96 | 32773
-156.958 | 100%N2 | 69.24 | 126.192 | 3595.8 | 0.22 | 10.34 | 375 | 10.63 | 400
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
13.65 | 90%CO2+10%Ar | 42.56 | 296.8 | 8989.09 | 0.27 | 11.08 | 1100 | 11.38 | 800
4.15 | 80%CO2+20%Ar | 43.85 | 287.3 | 10224.86 | 0.25 | 9.98 | 1350 | 9.92 | 1100
-6.72 | 70%CO2+30%Ar | 44.62 | 276.43 | 11540.39 | 0.23 | 10.92 | 1500 | 11.03 | 1300
-21.84 | 60%CO2+40%Ar | 47.08 | 261.31 | 12942.12 | 0.19 | 10.26 | 1800 | 10.59 | 2500
-43.92 | 50%CO2+50%Ar |  | 239.23 | 14718.17
-65.49 | 40%CO2+60%Ar |  | 217.66 | 24497
-85.34 | 30%CO2+70%Ar |  | 197.81 | 37613
-99.55 | 20%CO2+80%Ar |  | 183.6 | 15716
-117.12 | 10%CO2+90%Ar | 56.56 | 166.03 | 5314.43 | 0.2 | 9.97 | 200 | 9.76 | 500
-135.28 | 10%CO+90%Ar | 62.87 | 147.87 | 4756.86 | 0.2 |  | 275 |  | 250
-122.463 | 100%Ar | 62.01 | 150.687 | 5063 | 0.2 | 9.85 | 275 | 9.85 | 225
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
19.21 | 90%CO2+10%Ne | 41.47 | 302.36 | 10283.48 | 0.25 | 9.9 | 1500 | 10.43 | 900
16.99 | 80%CO2+20%Ne | 39.81 | 300.14 | 13723.48 | 0.17 | 10.25 | 2500 | 10.35 | 1000
70%CO2+30%Ne
60%CO2+40%Ne
50%CO2+50%Ne
40%CO2+60%Ne
30%CO2+70%Ne
20%CO2+80%Ne
10%CO2+90%Ne
100%Ne
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
15.26 | 90%CO2+10%Xe | 43.55 | 298.41 | 7977.87 | 0.25 | 10.11 | 850 | 10.36 | 650
9.51 | 80%CO2+20%Xe | 43.7 | 292.66 | 7168.4 | 0.25 | 10.16 | 725 | 9.55 | 600
4.6 | 70%CO2+30%Xe | 44.71 | 287.75 | 6816.4 | 0.28 | 10.28 | 650 | 9.91 | 700
1 | 60%CO2+40%Xe | 44.99 | 284.15 | 6513.52 | 0.28 | 10.45 | 550 | 9.72 | 700
-0.98 | 50%CO2+50%Xe | 44.17 | 282.17 | 6313.89 | 0.25 | 9.11 | 500 | 11 | 500
-1.33 | 40%CO2+60%Xe | 43.71 | 281.82 | 6216.14 | 0.25 | 9.31 | 425 | 10.71 | 525
-29.48 | 50%CO2+10%Xe+40%Ar | 49 | 253.67 | 11873.77 | 0.2 | 10.15 | 1350 | 9.72 | 2700
-37.06 | 40%CO2+15%Xe+45%Ar | 50.06 | 246.09 | 9922.52 | 0.28 | 10.27 | 1000 | 10.73 | 2000
-45.1 | 40%CO2+10%Xe+50%Ar | 51.44 | 238.05 | 11059.82 | 0.24 | 10.69 | 1100 | 10.22 | 2400
30%CO2+70%Xe
20%CO2+80%Xe
10%CO2+90%Xe
100%Xe

## Hoja2
Table 1. Replacing NF3 with Ar in the sCO2-NF3 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700 | CO
13.44 | 90%CO2+10%NF3 | 43.49 | 296.59 | 7935.27 | 0.26 | 11.77 | 1000 | 9.78 | 800 | Argon
4.24 | 80%CO2+20%NF3 | 45.05 | 287.39 | 7851.58 | 0.25 | 11.7 | 1200 | 9.76 | 900 | N2
-5.46 | 70%CO2+30%NF3 | 46.21 | 277.69 | 7482.4 | 0.23 | 12.11 | 1100 | 9.82 | 850
-8.36 | 67%CO2+33%NF3 | 46.48 | 274.79 | 7231.16 | 0.22 | 10.68 | 1150 | 9.85 | 750
-14.97 | 60%CO2+40%NF3 | 47.45 | 268.18 | 6935.24 | 0.22 | 10.83 | 1140 | 10.97 | 700
-18.59 | 56%CO2+44%NF3 | 48.45 | 264.56 | 6695.28 | 0.22 | 10.79 | 1150 | 9.68 | 800
-28.52 | 44%CO2+56%NF3 | 50.36 | 254.63 | 5998.71 | 0.22 | 10.02 | 1150 | 9.69 | 800
-37.9 | 30%CO2+70%NF3 | 52.25 | 245.25 | 5348.84 | 0.22 | 9.71 | 1150 | 9.89 | 800
-42.94 | 20%CO2+80%NF3 | 53.55 | 240.21 | 5024.3 | 0.22 | 11.38 | 1100 | 9.11 | 1000
-108.79 | 10%CO2+10%NF3+80%Ar | 58.2 | 174.36 | 5174.2 | 0.22 | 10.01 | 400 | 10.01 | 450
-93.45 | 20%CO2+10%NF3+70%Ar | 55.35 | 189.7 | 5425.63 | 0.22 | 11.14 | 450 | 10.45 | 500
-78.1 | 30%CO2+10%NF3+60%Ar | 53.71 | 205.05 | 5677.06 | 0.24 | 11.09 | 550 | 11 | 500
-52.02 | 47%CO2+10%NF3+43%Ar | 51.45 | 231.13 | 6104.49 | 0.27 | 10.22 | 700 | 9.78 | 700
-23.91 | 60%CO2+10%NF3+30%Ar | 47.69 | 259.24 | 10837.95 | 0.2 | 11.19 | 1350 | 10.95 | 1550
-8.84 | 70%CO2+10%NF3+20%Ar | 46.33 | 274.31 | 9793.14 | 0.25 | 11.04 | 1300 | 10.06 | 1400
3.34 | 80%CO2+10%NF3+10%Ar | 44.76 | 286.49 | 8846.17 | 0.26 | 10.99 | 1200 | 9.6 | 1100
13.41 | 90%CO2+5%NF3+5%Ar | 43.52 | 296.56 | 8448.02 | 0.27 | 10.43 | 1100 | 9.21 | 950
-29.15 | 100%NF3 | 47.22 | 254 | 7460.7 | 0.05 | 10.91 | 1800 | 9.85 | 400
-39.15 | 100%NF3 | 50.54 | 244 | 6060.7 | 0.14 | 10.52 | 1500 | 10.96 | 600
-49.15 | 100%NF3 | 54.07 | 234 | 4660.7 | 0.19 | 10.74 | 1150 | 10.57 | 700
Table 2. Lowering sCO2-NF3 Critical Temperature adding Ar
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-53.39 | 10%CO2+80%NF3+10%Ar | 54.45 | 229.76 | 4663.12 | 0.24 | 9.97 | 1150 | 10.63 | 1200
-60.76 | 10%CO2+70%NF3+20%Ar | 55.37 | 222.39 | 4684.77 | 0.25 | 10.49 | 1000 | 11.37 | 1200
-63.4 | 10%CO2+60%NF3+30%Ar | 53.66 | 219.75 | 4945.7 | 0.2 | 10.12 | 1000 | 9.85 | 850
-68.23 | 10%CO2+50%NF3+40%Ar | 54.91 | 214.92 | 5495.66 | 0.22 | 9.55 | 1000 | 9.61 | 1000
-73.17 | 10%CO2+40%NF3+50%Ar | 55.11 | 209.98 | 6035.43 | 0.22 | 10.65 | 900 | 10.68 | 900
-79.1 | 10%CO2+30%NF3+60%Ar | 55.82 | 204.05 | 6649.19 | 0.22 | 9.91 | 900 | 10.42 | 800
-86.78 | 10%CO2+20%NF3+70%Ar | 56.82 | 196.37 | 7283.13 | 0.22 | 10.54 | 800 | 10.32 | 700
-108.79 | 10%CO2+10%NF3+80%Ar | 58.57 | 174.36 | 5274.2 | 0.23 | 10.14 | 400 | 10.39 | 500
Table 3. Replacing CF4 with Ar in the sCO2-CF4 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-109.44 | 10%CO2+10%CF4+80%Ar | 59.28 | 173.71 | 5203.13 | 0.2 | 10.83 | 450 | 9.96 | 375
-94.1 | 20%CO2+10%CF4+70%Ar | 56.02 | 189.05 | 5454.56 | 0.2 | 10.31 | 550 | 10.41 | 400
-78.75 | 30%CO2+10%CF4+60%Ar | 54.78 | 204.4 | 5605.99 | 0.25 | 10.47 | 600 | 10.58 | 600
-63.41 | 40%CO2+10%CF4+50%Ar | 53.03 | 219.74 | 5857.42 | 0.26 | 9.89 | 700 | 10.79 | 600
-48.07 | 50%CO2+10%CF4+40%Ar | 51.12 | 235.08 | 6108.85 | 0.26 | 10.56 | 750 | 11.16 | 600
-40.39 | 55%CO2+10%CF4+35%Ar | 50.06 | 242.76 | 6234.56 | 0.26 | 11.54 | 750 | 11.75 | 600
-23.37 | 60%CO2+10%CF4+30%Ar | 48.12 | 259.78 | 10610.41 | 0.22 | 10.03 | 1500 | 11.25 | 1500
-8.89 | 70%CO2+10%CF4+20%Ar | 46.32 | 274.26 | 9715.61 | 0.24 | 10.34 | 1400 | 10.4 | 1200
2.88 | 80%CO2+10%CF4+10%Ar | 44.7 | 286.03 | 8788.54 | 0.24 | 9.62 | 1300 | 9.85 | 900
13.12 | 90%CO2+5%CF4+5%Ar | 43.24 | 296.27 | 8317.03 | 0.26 | 10.7 | 1100 | 10.18 | 800
Table 4. Lowering sCO2-CF4 Critical Temperature adding Ar
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-57.28 | 10%CO2+80%CF4+10%Ar | 55.94 | 225.87 | 4265.36 | 0.21 | 9.93 | 1550 | 10.13 | 1500
-60.83 | 10%CO2+70%CF4+20%Ar | 56.73 | 222.32 | 4846.6 | 0.21 | 11.08 | 1400 | 9.52 | 1500
-64.71 | 10%CO2+60%CF4+30%Ar | 56.67 | 218.44 | 5271.63 | 0.22 | 10.36 | 1400 | 10.95 | 1500
-69.04 | 10%CO2+50%CF4+40%Ar | 56.79 | 214.11 | 5645.17 | 0.215 | 10.3 | 1300 | 10.28 | 1500
-73.96 | 10%CO2+40%CF4+50%Ar | 57.22 | 209.19 | 6169.03 | 0.215 | 10.32 | 1200 | 9.74 | 1450
-79.77 | 10%CO2+30%CF4+60%Ar | 57.75 | 203.38 | 6735.39 | 0.22 | 10.1 | 1100 | 9.64 | 1300
-78.51 | 10%CO2+20%CF4+70%Ar | 55.57 | 204.64 | 7708.56 | 0.2 | 11.32 | 1000 | 10.35 | 1300
-109.44 | 10%CO2+10%CF4+80%Ar | 59.11 | 173.71 | 5103.13 | 0.21 | 10.29 | 450 | 10.92 | 400
Table 5. Replacing CH4 with Ar in the sCO2-CH4 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
13.35 | 90%CO2+10%CH4 | 43.03 | 296.5 | 8281.61 | 0.26 | 10.97 | 1050 | 10.86 | 700
4.1 | 80%CO2+20%CH4 | 44.41 | 287.25 | 8766.79 | 0.24 | 9.97 | 1200 | 10.99 | 850
-6.16 | 70%CO2+30%CH4 | 45.25 | 276.99 | 8989.2 | 0.2 | 9.79 | 1300 | 10.18 | 700
-17.71 | 60%CO2+40%CH4 | 47.29 | 265.44 | 9055.31 | 0.2 | 10.69 | 1350 | 9.95 | 850
-30.5 | 50%CO2+50%CH4 | 50.53 | 252.65 | 8692.27 | 0.2 | 10.4 | 1200 | 11.5 | 800
-44.02 | 36%CO2+64%CH4 | 51.41 | 239.13 | 8027.37 | 0.2 | 11.71 | 1400 | 10.34 | 675
-56.97 | 30%CO2+70%CH4 | 53.94 | 226.18 | 7111.83 | 0.2 | 11.61 | 1100 | 10.17 | 525
-69.56 | 20%CO2+80%CH4 | 55.11 | 213.59 | 6335.04 | 0.15 | 10.26 | 950 | 10.88 | 350
-113.14 | 10%CO2+10%CH4+80%Ar | 57.39 | 170.01 | 5288.05 | 0.21 | 10.06 | 175 | 10.11 | 700
-97.79 | 20%CO2+10%CH4+70%Ar | 55.33 | 185.36 | 5439.48 | 0.21 | 10.48 | 400 | 10.63 | 400
-82.45 | 30%CO2+10%CH4+60%Ar | 54.46 | 200.7 | 5790.91 | 0.28 | 10.5 | 500 | 11.65 | 700
-67.1 | 40%CO2+10%CH4+50%Ar | 52.2 | 216.05 | 5942.34 | 0.25 | 10.26 | 600 | 10.97 | 450
-50.95 | 45%CO2+10%CH4+45%Ar | 50.95 | 232.2 | 13037.74 | 0.1 | 11.02 | 1600 | 12.08 | 2600
-39.14 | 50%CO2+10%CH4+40%Ar | 49.81 | 244.01 | 12657.38 | 0.14 | 10.01 | 1700 | 10.41 | 2700
-19.98 | 60%CO2+10%CH4+30%Ar | 47.43 | 263.17 | 11738.61 | 0.25 | 11.37 | 1600 | 12.09 | 2000
-6.75 | 70%CO2+10%CH4+20%Ar | 45.66 | 276.4 | 10574.46 | 0.25 | 11.57 | 1400 | 10.63 | 1400
3.97 | 80%CO2+10%CH4+10%Ar | 44.3 | 287.12 | 9453.29 | 0.25 | 10.02 | 1300 | 9.78 | 1000
-81.7 | 10%CO2+90%CH4 | 57.9 | 201.45 | 5461.41 | 0.17 | 9.62 | 900 | 10.74 | 350
-92.59 | 100%CH4 | 61.09 | 190.56 | 4799.2 | 0.2
Table 6. Lowering sCO2-CH4 Critical Temperature adding Ar
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-83.75 | 10%CO2+80%CH4+10%Ar | 59.51 | 199.4 | 5834.56 | 0.25 | 10.91 | 1000 | 10.17 | 1000
-86.66 | 10%CO2+70%CH4+20%Ar | 59.03 | 196.49 | 6048.91 | 0.25 | 10.4 | 1000 | 10.78 | 1000
-93.2 | 10%CO2+60%CH4+30%Ar | 58.07 | 189.95 | 5056.15 | 0.215 | 9.76 | 750 | 10.55 | 900
-91.77 | 10%CO2+50%CH4+40%Ar | 59.45 | 191.38 | 6677.05 | 0.24 | 11.27 | 850 | 10.38 | 750
-95.03 | 10%CO2+40%CH4+50%Ar | 59.67 | 188.12 | 6930.26 | 0.24 | 10.89 | 800 | 10.25 | 700
-105.16 | 10%CO2+30%CH4+60%Ar | 57.71 | 177.99 | 5235.29 | 0.2 | 10.18 | 450 | 10.18 | 700
-109.15 | 10%CO2+20%CH4+70%Ar | 57.47 | 174 | 5161.67 | 0.2 | 9.95 | 300 | 9.91 | 700
-113.14 | 10%CO2+10%CH4+80%Ar | 57.39 | 170.01 | 5288.05 | 0.21 | 10.06 | 175 | 10.11 | 700
Table 7. Increasing sCO2-Kr power cycle efficiency by adding Ar
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
12.85 | 90%CO2+10%Kr | 42.72 | 296 | 7953.13 | 0.25 | 9.78 | 900 | 11.06 | 550
3.49 | 80%CO2+20%Kr | 43.73 | 286.64 | 7971.48 | 0.23 | 10.93 | 800 | 10.49 | 550
-6.37 | 70%CO2+30%Kr | 45.41 | 276.78 | 7806.3 | 0.24 | 10.06 | 750 | 9.99 | 600
-15.9 | 60%CO2+40%Kr | 47.12 | 267.25 | 7493.5 | 0.27 | 9.75 | 700 | 10.38 | 750
-24.55 | 50%CO2+50%Kr | 47.82 | 258.6 | 7237.87 | 0.25 | 9.95 | 600 | 10.13 | 550
-32.76 | 40%CO2+60%Kr | 48.07 | 250.39 | 7024.97 | 0.22 | 10.64 | 500 | 10.61 | 425
-39.92 | 30%CO2+70%Kr | 48.71 | 243.23 | 6908.85 | 0.22 | 10.89 | 450 | 10.09 | 425
-47.93 | 20%CO2+80%Kr | 49.03 | 235.22 | 6845.67 | 0.2 | 10.89 | 400 | 9.96 | 375
-58.27 | 10%CO2+90%Kr | 49.88 | 224.88 | 6588.89 | 0.2 | 10.1 | 350 | 9.97 | 350
-61.47 | 10%CO2+80%Kr+10%Ar | 50.73 | 221.68 | 7044.6 | 0.23 | 11.36 | 350 | 9.88 | 500
-65.43 | 10%CO2+70%Kr+20%Ar | 51.68 | 217.72 | 7518.9 | 0.23 | 11.72 | 400 | 9.74 | 550
-70.08 | 10%CO2+60%Kr+30%Ar | 52.59 | 213.07 | 7909.1 | 0.23 | 10.77 | 475 | 10.19 | 550
-75.42 | 10%CO2+50%Kr+40%Ar | 53.71 | 207.73 | 8300.2 | 0.23 | 9.79 | 550 | 10.36 | 550
-81.45 | 10%CO2+40%Kr+50%Ar | 54.94 | 201.7 | 8368.6 | 0.23 | 10.29 | 550 | 9.65 | 600
-88.1 | 10%CO2+30%Kr+60%Ar | 56.19 | 195.05 | 8489.8 | 0.23 | 9.93 | 575 | 9.63 | 600
-95.29 | 10%CO2+20%Kr+70%Ar | 57.43 | 187.86 | 8347.7 | 0.23 | 9.73 | 575 | 9.56 | 575
-111.24 | 10%CO2+10%Kr+80%Ar | 55.41 | 171.91 | 5380.63 | 0.17 | 10.85 | 300 | 11.88 | 300
-114.18 | 10%CO2+5%Kr+85%Ar | 56.3 | 168.97 | 5347.5 | 0.2 | 10.44 | 200 | 11.15 | 450
-81.45 | 10%CO2+40%Kr+50%Ar | 55.23 | 201.7 | 8368.68 | 0.25 | 10.2 | 550 | 10.05 | 700
-63.8 | 20%CO2+40%Kr+40%Ar | 52.91 | 219.35 | 9261.73 | 0.25 | 10.75 | 700 | 10.89 | 800
-55.9 | 25%CO2+40%Kr+35%Ar | 52.01 | 227.25 | 9408.89 | 0.25 | 10.76 | 750 | 10.38 | 900
-48.63 | 30%CO2+40%Kr+30%Ar | 50.77 | 234.52 | 9291.4 | 0.25 | 9.92 | 800 | 11 | 800
-35.89 | 40%CO2+40%Kr+20%Ar | 49.16 | 247.26 | 9000.91 | 0.25 | 10.45 | 800 | 10.62 | 800
-24.9 | 50%CO2+40%Kr+10%Ar | 47.7 | 258.25 | 8298.63 | 0.25 | 10.55 | 750 | 10.35 | 700
-20.27 | 55%CO2+40%Kr+5%Ar | 47.28 | 262.88 | 7858.15 | 0.25 | 10.67 | 700 | 10.25 | 650
-95.9 | 20%CO2+10%Kr+70%Ar | 53.22 | 187.25 | 5532.06 | 0.15 | 10.91 | 375 | 11.13 | 225
-80.56 | 30%CO2+10%Kr+60%Ar | 52.95 | 202.59 | 5883.49 | 0.25 | 10.76 | 450 | 11.04 | 450
-57.78 | 40%CO2+10%Kr+50%Ar | 52.45 | 225.37 | 12815.23 | 0.1 | 9.65 | 1400 | 11.09 | 3250
-36.16 | 50%CO2+10%Kr+40%Ar | 48.79 | 246.99 | 12496.52 | 0.18 | 10.29 | 1450 | 11.62 | 1750
-19.18 | 60%CO2+10%Kr+30%Ar | 47.3 | 263.97 | 11388.72 | 0.25 | 10.38 | 1400 | 11.04 | 1700
-6.81 | 70%CO2+10%Kr+20%Ar | 45.37 | 276.34 | 10238.64 | 0.25 | 10.94 | 1200 | 10.68 | 1100
3.86 | 80%CO2+10%Kr+10%Ar | 43.8 | 287.01 | 9092 | 0.25 | 10.81 | 1050 | 10.53 | 800
8.62 | 85%CO2+10%Kr+5%Ar | 43.48 | 291.77 | 8490.5 | 0.25 | 10 | 1000 | 9.41 | 750
-73.67 | 100%Kr | 50.89 | 209.48 | 5725 | 0.15 | 10.21 | 250 | 9.93 | 250
Table 8. Increasing sCO2-Xe power cycle efficiency by adding Ar
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
14.39 | 90%CO2+5%Xe+5%Ar | 42.67 | 297.54 | 8095.71 | 0.25 | 10.53 | 950 | 9.4 | 700
6.22 | 80%CO2+10%Xe+10%Ar | 43.44 | 289.37 | 8385.99 | 0.24 | 10.1 | 950 | 9.8 | 700
-4.57 | 70%CO2+10%Xe+20%Ar | 45.12 | 278.58 | 9266.78 | 0.24 | 11.31 | 1000 | 9.18 | 1000
-16.38 | 60%CO2+10%Xe+30%Ar | 45.89 | 266.77 | 10065.44 | 0.2 | 9.77 | 1100 | 9.79 | 850
-29.48 | 50%CO2+10%Xe+40%Ar | 49 | 253.67 | 11873.77 | 0.2 | 11.06 | 1300 | 9.72 | 2800
-45.1 | 40%CO2+10%Xe+50%Ar | 51.44 | 238.05 | 11059.82 | 0.24 | 10.69 | 1100 | 10.22 | 2400
-59.25 | 30%CO2+10%Xe+60%Ar | 53.44 | 223.9 | 10807.19 | 0.25 | 10.59 | 1000 | 10.45 | 2200
-72.99 | 20%CO2+10%Xe+70%Ar | 55.27 | 210.16 | 10112.03 | 0.26 | 11.48 | 800 | 10.05 | 1800
-88.77 | 10%CO2+10%Xe+80%Ar | 56.14 | 194.38 | 9047.48 | 0.22 | 9.93 | 650 | 9.95 | 650
-106.78 | 10%Xe+90%Ar | 57.98 | 176.37 | 7626.91 | 0.22 | 10.01 | 450 | 10.58 | 450
-132.47 | 100%Ar | 62.34 | 150.68 | 4963 | 0.22 | 10.87 | 250 | 9.98 | 275
15.26 | 90%CO2+10%Xe | 43.55 | 298.41 | 7977.87 | 0.25 | 10.11 | 850 | 10.36 | 650
9.51 | 80%CO2+20%Xe | 43.7 | 292.66 | 7168.4 | 0.25 | 10.16 | 725 | 9.55 | 600
4.6 | 70%CO2+30%Xe | 44.71 | 287.75 | 6816.4 | 0.28 | 10.28 | 650 | 9.91 | 700
1 | 60%CO2+40%Xe | 44.99 | 284.15 | 6513.52 | 0.28 | 10.45 | 550 | 9.72 | 700
-0.98 | 50%CO2+50%Xe | 44.17 | 282.17 | 6313.89 | 0.25 | 9.11 | 500 | 11 | 500
-1.33 | 40%CO2+60%Xe | 43.71 | 281.82 | 6216.14 | 0.25 | 9.31 | 425 | 10.71 | 525
100%Xe
Table 9. Replacing NF3 with N2 in the sCO2-NF3 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
13.44 | 90%CO2+10%NF3 | 43.49 | 296.59 | 7935.27 | 0.26 | 11.77 | 1000 | 9.78 | 800
4.24 | 80%CO2+20%NF3 | 45.05 | 287.39 | 7851.58 | 0.25 | 11.7 | 1200 | 9.76 | 900
-5.46 | 70%CO2+30%NF3 | 46.21 | 277.69 | 7482.4 | 0.23 | 12.11 | 1100 | 9.82 | 850
-8.36 | 67%CO2+33%NF3 | 46.48 | 274.79 | 7231.16 | 0.22 | 10.68 | 1150 | 9.85 | 750
-14.97 | 60%CO2+40%NF3 | 47.45 | 268.18 | 6935.24 | 0.22 | 10.83 | 1140 | 10.97 | 700
-18.59 | 56%CO2+44%NF3 | 48.45 | 264.56 | 6695.28 | 0.22 | 10.79 | 1150 | 9.68 | 800
-28.52 | 44%CO2+56%NF3 | 50.36 | 254.63 | 5998.71 | 0.22 | 10.02 | 1150 | 9.69 | 800
-37.9 | 30%CO2+70%NF3 | 52.25 | 245.25 | 5348.84 | 0.22 | 9.71 | 1150 | 9.89 | 800
-42.94 | 20%CO2+80%NF3 | 53.55 | 240.21 | 5024.3 | 0.22 | 11.38 | 1100 | 9.11 | 1000
-283.15 | 10%CO2+10%NF3+80%N2
-283.15 | 20%CO2+10%NF3+70%N2
-283.15 | 30%CO2+10%NF3+60%N2
-283.15 | 40%CO2+10%NF3+50%N2
-111.11 | 5%CO2+10%NF3+20%N2+65%Ar | 61 | 172.04 | 6850.6 | 0.24 | 10.15 | 650 | 10.51 | 700
-113.69 | 10%CO2+10%NF3+20%N2+60%Ar | 59.5 | 169.46 | 4980.7 | 0.23 | 10.35 | 400 | 10.49 | 600
-98.35 | 20%CO2+10%NF3+20%N2+50%Ar | 56.53 | 184.8 | 5232.1 | 0.24 | 10.52 | 500 | 11.48 | 600
-83 | 30%CO2+10%NF3+20%N2+40%Ar | 54.92 | 200.15 | 5383.6 | 0.25 | 10.19 | 600 | 10.22 | 600
-67.66 | 40%CO2+10%NF3+20%N2+30%Ar | 53.18 | 215.49 | 5635 | 0.25 | 10.64 | 650 | 9.66 | 600
-43.14 | 50%CO2+10%NF3+20%N2+20%Ar | 50.32 | 240.01 | 12324.9 | 0.1 |  | 1800 |  | 2750
-45.35 | 50%CO2+10%NF3+40%N2 | 49.94 | 237.8 | 13342.7 | 0.05 | 10.82 | 2300 | 11.29 | 2750
-26.44 | 60%CO2+10%NF3+30%N2 | 47.87 | 256.71 | 11733.2 | 0.15 | 9.57 | 1900 | 10.58 | 2000
-11.29 | 70%CO2+10%NF3+20%N2 | 46.3 | 271.86 | 10268.17 | 0.21 | 10.33 | 1500 | 9.7 | 1500
2.06 | 80%CO2+10%NF3+10%N2 | 44.59 | 285.21 | 8990.15 | 0.25 | 10.9 | 1250 | 10.61 | 1000
12.71 | 90%CO2+5%NF3+5%N2 | 43.6 | 295.86 | 8380.1 | 0.28 | 11.42 | 1100 | 9.91 | 1000
-29.15 | 100%NF3 | 47.22 | 254 | 7460.7 | 0.05 | 10.91 | 1800 | 9.85 | 400
-39.15 | 100%NF3 | 50.54 | 244 | 6060.7 | 0.14 | 10.52 | 1500 | 10.96 | 600
-49.15 | 100%NF3 | 54.07 | 234 | 4660.7 | 0.19 | 10.74 | 1150 | 10.57 | 700
-156.958 | 100%N2 | 69.24 | 126.192 | 3595.8 | 0.22 | 10.34 | 375 | 10.63 | 400
Table 10. Replacing NF3 with CO in the sCO2-NF3 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
13.44 | 90%CO2+10%NF3 | 43.49 | 296.59 | 7935.27 | 0.26 | 11.77 | 1000 | 9.78 | 800
4.24 | 80%CO2+20%NF3 | 45.05 | 287.39 | 7851.58 | 0.25 | 11.7 | 1200 | 9.76 | 900
-5.46 | 70%CO2+30%NF3 | 46.21 | 277.69 | 7482.4 | 0.23 | 12.11 | 1100 | 9.82 | 850
-8.36 | 67%CO2+33%NF3 | 46.48 | 274.79 | 7231.16 | 0.22 | 10.68 | 1150 | 9.85 | 750
-14.97 | 60%CO2+40%NF3 | 47.45 | 268.18 | 6935.24 | 0.22 | 10.83 | 1140 | 10.97 | 700
-18.59 | 56%CO2+44%NF3 | 48.45 | 264.56 | 6695.28 | 0.22 | 10.79 | 1150 | 9.68 | 800
-28.52 | 44%CO2+56%NF3 | 50.36 | 254.63 | 5998.71 | 0.22 | 10.02 | 1150 | 9.69 | 800
-37.9 | 30%CO2+70%NF3 | 52.25 | 245.25 | 5348.84 | 0.22 | 9.71 | 1150 | 9.89 | 800
-42.94 | 20%CO2+80%NF3 | 53.55 | 240.21 | 5024.3 | 0.22 | 11.38 | 1100 | 9.11 | 1000
-283.15 | 10%CO2+10%NF3+80%CO
-283.15 | 20%CO2+10%NF3+70%CO
-283.15 | 30%CO2+10%NF3+60%CO
-283.15 | 47%CO2+10%NF3+43%CO
-283.15 | 60%CO2+10%NF3+30%CO
-10.64 | 70%CO2+10%NF3+20%CO | 46.15 | 272.51 | 9594.07 | 0.21 | 10.81 | 1300 | 9.41 | 1200
-283.15 | 80%CO2+10%NF3+10%CO
-283.15 | 90%CO2+5%NF3+5%CO
-29.15 | 100%NF3 | 47.22 | 254 | 7460.7 | 0.05 | 10.91 | 1800 | 9.85 | 400
-39.15 | 100%NF3 | 50.54 | 244 | 6060.7 | 0.14 | 10.52 | 1500 | 10.96 | 600
-49.15 | 100%NF3 | 54.07 | 234 | 4660.7 | 0.19 | 10.74 | 1150 | 10.57 | 700
-156.958 | 100%N2 | 69.24 | 126.192 | 3595.8 | 0.22 | 10.34 | 375 | 10.63 | 400
Table 11. Lowering sCO2-NF3 Critical Temperature adding N2
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 10%CO2+80%NF3+10%N2
-283.15 | 10%CO2+70%NF3+20%N2
-283.15 | 10%CO2+60%NF3+30%N2
-283.15 | 10%CO2+50%NF3+40%N2
-283.15 | 10%CO2+40%NF3+50%N2
-283.15 | 10%CO2+30%NF3+60%N2
-283.15 | 10%CO2+20%NF3+70%N2
-283.15 | 10%CO2+10%NF3+80%N2
Table 12. Lowering sCO2-NF3 Critical Temperature adding CO
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 10%CO2+80%NF3+10%CO
-283.15 | 10%CO2+70%NF3+20%CO
-283.15 | 10%CO2+60%NF3+30%CO
-283.15 | 10%CO2+50%NF3+40%CO
-283.15 | 10%CO2+40%NF3+50%CO
-283.15 | 10%CO2+30%NF3+60%CO
-283.15 | 10%CO2+20%NF3+70%CO
-283.15 | 10%CO2+10%NF3+80%CO
Table 13. Lowering sCO2-CF4 Critical Temperature adding N2
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 10%CO2+80%CF4+10%N2
-283.15 | 10%CO2+70%CF4+20%N2
-283.15 | 10%CO2+60%CF4+30%N2
-283.15 | 10%CO2+50%CF4+40%N2
-283.15 | 10%CO2+40%CF4+50%N2
-283.15 | 10%CO2+30%CF4+60%N2
-283.15 | 10%CO2+20%CF4+70%N2
-283.15 | 10%CO2+10%CF4+80%N2
Table 14. Lowering sCO2-CF4 Critical Temperature adding CO
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 10%CO2+80%NF3+10%CO
-283.15 | 10%CO2+70%NF3+20%CO
-283.15 | 10%CO2+60%NF3+30%CO
-283.15 | 10%CO2+50%NF3+40%CO
-283.15 | 10%CO2+40%NF3+50%CO
-283.15 | 10%CO2+30%NF3+60%CO
-283.15 | 10%CO2+20%NF3+70%CO
-283.15 | 10%CO2+10%NF3+80%CO
Table 15. Replacing CH4 with N2 in the sCO2-CH4 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
13.35 | 90%CO2+10%CH4 | 43.03 | 296.5 | 8281.61 | 0.26 | 10.97 | 1050 | 10.86 | 700
4.1 | 80%CO2+20%CH4 | 44.41 | 287.25 | 8766.79 | 0.24 | 9.97 | 1200 | 10.99 | 850
-6.16 | 70%CO2+30%CH4 | 45.25 | 276.99 | 8989.2 | 0.2 | 9.79 | 1300 | 10.18 | 700
-17.71 | 60%CO2+40%CH4 | 47.29 | 265.44 | 9055.31 | 0.2 | 10.69 | 1350 | 9.95 | 850
-30.5 | 50%CO2+50%CH4 | 50.53 | 252.65 | 8692.27 | 0.2 | 10.4 | 1200 | 11.5 | 800
-44.02 | 36%CO2+64%CH4 | 51.41 | 239.13 | 8027.37 | 0.2 | 11.71 | 1400 | 10.34 | 675
-56.97 | 30%CO2+70%CH4 | 53.94 | 226.18 | 7111.83 | 0.2 | 11.61 | 1100 | 10.17 | 525
-69.56 | 20%CO2+80%CH4 | 55.11 | 213.59 | 6335.04 | 0.15 | 10.26 | 950 | 10.88 | 350
-283.15 | 10%CO2+10%CH4+80%Ar
-283.15 | 20%CO2+10%CH4+70%Ar
-283.15 | 30%CO2+10%CH4+60%Ar
-283.15 | 40%CO2+10%CH4+50%Ar
-283.15 | 45%CO2+10%CH4+45%Ar
-283.15 | 50%CO2+10%CH4+40%Ar
-283.15 | 60%CO2+10%CH4+30%Ar
-283.15 | 70%CO2+10%CH4+20%Ar
-283.15 | 80%CO2+10%CH4+10%Ar
-81.7 | 10%CO2+90%CH4 | 57.9 | 201.45 | 5461.41 | 0.17 | 9.62 | 900 | 10.74 | 350
-92.59 | 100%CH4 | 61.09 | 190.56 | 4799.2 | 0.2
Table 16. Lowering sCO2-CH4 Critical Temperature adding N2
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 10%CO2+80%CH4+10%Ar | 59.16
-283.15 | 10%CO2+70%CH4+20%Ar | 60.12
-283.15 | 10%CO2+60%CH4+30%Ar | 60.02
-283.15 | 10%CO2+50%CH4+40%Ar | 60.65
-283.15 | 10%CO2+40%CH4+50%Ar | 61.23
-283.15 | 10%CO2+30%CH4+60%Ar | 53.47
-283.15 | 10%CO2+20%CH4+70%Ar | 53.15
-283.15 | 10%CO2+10%CH4+80%Ar | 52.29
Table 17. Replacing CH4 with CO in the sCO2-CH4 Blend
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
13.35 | 90%CO2+10%CH4 | 43.03 | 296.5 | 8281.61 | 0.26 | 10.97 | 1050 | 10.86 | 700
4.1 | 80%CO2+20%CH4 | 44.41 | 287.25 | 8766.79 | 0.24 | 9.97 | 1200 | 10.99 | 850
-6.16 | 70%CO2+30%CH4 | 45.25 | 276.99 | 8989.2 | 0.2 | 9.79 | 1300 | 10.18 | 700
-17.71 | 60%CO2+40%CH4 | 47.29 | 265.44 | 9055.31 | 0.2 | 10.69 | 1350 | 9.95 | 850
-30.5 | 50%CO2+50%CH4 | 50.53 | 252.65 | 8692.27 | 0.2 | 10.4 | 1200 | 11.5 | 800
-44.02 | 36%CO2+64%CH4 | 51.41 | 239.13 | 8027.37 | 0.2 | 11.71 | 1400 | 10.34 | 675
-56.97 | 30%CO2+70%CH4 | 53.94 | 226.18 | 7111.83 | 0.2 | 11.61 | 1100 | 10.17 | 525
-69.56 | 20%CO2+80%CH4 | 55.11 | 213.59 | 6335.04 | 0.15 | 10.26 | 950 | 10.88 | 350
-283.15 | 10%CO2+10%CH4+80%Ar
-283.15 | 20%CO2+10%CH4+70%Ar
-283.15 | 30%CO2+10%CH4+60%Ar
-283.15 | 40%CO2+10%CH4+50%Ar
-283.15 | 45%CO2+10%CH4+45%Ar
-283.15 | 50%CO2+10%CH4+40%Ar
-283.15 | 60%CO2+10%CH4+30%Ar
-283.15 | 70%CO2+10%CH4+20%Ar
-283.15 | 80%CO2+10%CH4+10%Ar
-81.7 | 10%CO2+90%CH4 | 57.9 | 201.45 | 5461.41 | 0.17 | 9.62 | 900 | 10.74 | 350
-92.59 | 100%CH4 | 61.09 | 190.56 | 4799.2 | 0.2
Table 18. Lowering sCO2-CH4 Critical Temperature adding CO
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 10%CO2+80%CH4+10%Ar
-283.15 | 10%CO2+70%CH4+20%Ar
-283.15 | 10%CO2+60%CH4+30%Ar
-283.15 | 10%CO2+50%CH4+40%Ar
-283.15 | 10%CO2+40%CH4+50%Ar
-283.15 | 10%CO2+30%CH4+60%Ar
-283.15 | 10%CO2+20%CH4+70%Ar
-283.15 | 10%CO2+10%CH4+80%Ar
Table 19. Increasing sCO2-Kr power cycle efficiency by adding N2
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
12.85 | 90%CO2+10%Kr | 42.72 | 296 | 7953.13 | 0.25 | 9.78 | 900 | 11.06 | 550
3.49 | 80%CO2+20%Kr | 43.73 | 286.64 | 7971.48 | 0.23 | 10.93 | 800 | 10.49 | 550
-6.37 | 70%CO2+30%Kr | 45.41 | 276.78 | 7806.3 | 0.24 | 10.06 | 750 | 9.99 | 600
-15.9 | 60%CO2+40%Kr | 47.12 | 267.25 | 7493.5 | 0.27 | 9.75 | 700 | 10.38 | 750
-24.55 | 50%CO2+50%Kr | 47.82 | 258.6 | 7237.87 | 0.25 | 9.95 | 600 | 10.13 | 550
-32.76 | 40%CO2+60%Kr | 48.07 | 250.39 | 7024.97 | 0.22 | 10.64 | 500 | 10.61 | 425
-39.92 | 30%CO2+70%Kr | 48.71 | 243.23 | 6908.85 | 0.22 | 10.89 | 450 | 10.09 | 425
-47.93 | 20%CO2+80%Kr | 49.03 | 235.22 | 6845.67 | 0.2 | 10.89 | 400 | 9.96 | 375
-58.27 | 10%CO2+90%Kr | 49.88 | 224.88 | 6588.89 | 0.2 | 10.1 | 350 | 9.97 | 350
-283.15 | 10%CO2+40%Kr+50%Ar
-283.15 | 20%CO2+40%Kr+40%Ar
-283.15 | 25%CO2+40%Kr+35%Ar
-283.15 | 30%CO2+40%Kr+30%Ar
-283.15 | 40%CO2+40%Kr+20%Ar
-283.15 | 50%CO2+40%Kr+10%Ar
-283.15 | 55%CO2+40%Kr+5%Ar
-283.15 | 20%CO2+10%Kr+70%Ar
-283.15 | 30%CO2+10%Kr+60%Ar
-283.15 | 40%CO2+10%Kr+50%Ar
-283.15 | 50%CO2+10%Kr+40%Ar
-283.15 | 60%CO2+10%Kr+30%Ar
-283.15 | 70%CO2+10%Kr+20%Ar
-283.15 | 80%CO2+10%Kr+10%Ar
-283.15 | 85%CO2+10%Kr+5%Ar
-73.67 | 100%Kr | 50.89 | 209.48 | 5725 | 0.15 | 10.21 | 250 | 9.93 | 250
Table 20. Increasing sCO2-Kr power cycle efficiency by adding CO
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
12.85 | 90%CO2+10%Kr | 42.72 | 296 | 7953.13 | 0.25 | 9.78 | 900 | 11.06 | 550
3.49 | 80%CO2+20%Kr | 43.73 | 286.64 | 7971.48 | 0.23 | 10.93 | 800 | 10.49 | 550
-6.37 | 70%CO2+30%Kr | 45.41 | 276.78 | 7806.3 | 0.24 | 10.06 | 750 | 9.99 | 600
-15.9 | 60%CO2+40%Kr | 47.12 | 267.25 | 7493.5 | 0.27 | 9.75 | 700 | 10.38 | 750
-24.55 | 50%CO2+50%Kr | 47.82 | 258.6 | 7237.87 | 0.25 | 9.95 | 600 | 10.13 | 550
-32.76 | 40%CO2+60%Kr | 48.07 | 250.39 | 7024.97 | 0.22 | 10.64 | 500 | 10.61 | 425
-39.92 | 30%CO2+70%Kr | 48.71 | 243.23 | 6908.85 | 0.22 | 10.89 | 450 | 10.09 | 425
-47.93 | 20%CO2+80%Kr | 49.03 | 235.22 | 6845.67 | 0.2 | 10.89 | 400 | 9.96 | 375
-58.27 | 10%CO2+90%Kr | 49.88 | 224.88 | 6588.89 | 0.2 | 10.1 | 350 | 9.97 | 350
-283.15 | 10%CO2+40%Kr+50%Ar
-283.15 | 20%CO2+40%Kr+40%Ar
-283.15 | 25%CO2+40%Kr+35%Ar
-283.15 | 30%CO2+40%Kr+30%Ar
-283.15 | 40%CO2+40%Kr+20%Ar
-283.15 | 50%CO2+40%Kr+10%Ar | 51.55
-283.15 | 55%CO2+40%Kr+5%Ar
-283.15 | 20%CO2+10%Kr+70%Ar
-283.15 | 30%CO2+10%Kr+60%Ar
-283.15 | 40%CO2+10%Kr+50%Ar
-283.15 | 50%CO2+10%Kr+40%Ar
-283.15 | 60%CO2+10%Kr+30%Ar
-283.15 | 70%CO2+10%Kr+20%Ar
-283.15 | 80%CO2+10%Kr+10%Ar | 47.07
-283.15 | 85%CO2+10%Kr+5%Ar
-73.67 | 100%Kr | 50.89 | 209.48 | 5725 | 0.15 | 10.21 | 250 | 9.93 | 250
Table 21. Increasing sCO2-Xe power cycle efficiency by adding N2
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 90%CO2+5%Xe+5%Ar
-283.15 | 80%CO2+10%Xe+10%Ar | 47.22
-283.15 | 70%CO2+10%Xe+20%Ar
-283.15 | 60%CO2+10%Xe+30%Ar
-283.15 | 50%CO2+10%Xe+40%Ar
-283.15 | 40%CO2+10%Xe+50%Ar
-283.15 | 30%CO2+10%Xe+60%Ar | 53.63
-283.15 | 20%CO2+10%Xe+70%Ar
-283.15 | 10%CO2+10%Xe+80%Ar
-106.78 | 10%Xe+90%Ar | 57.98 | 176.37 | 7626.91 | 0.22 | 10.01 | 450 | 10.58 | 450
-132.47 | 100%Ar | 62.34 | 150.68 | 4963 | 0.22 | 10.87 | 250 | 9.98 | 275
15.26 | 90%CO2+10%Xe | 43.55 | 298.41 | 7977.87 | 0.25 | 10.11 | 850 | 10.36 | 650
9.51 | 80%CO2+20%Xe | 43.7 | 292.66 | 7168.4 | 0.25 | 10.16 | 725 | 9.55 | 600
4.6 | 70%CO2+30%Xe | 44.71 | 287.75 | 6816.4 | 0.28 | 10.28 | 650 | 9.91 | 700
1 | 60%CO2+40%Xe | 44.99 | 284.15 | 6513.52 | 0.28 | 10.45 | 550 | 9.72 | 700
-0.98 | 50%CO2+50%Xe | 44.17 | 282.17 | 6313.89 | 0.25 | 9.11 | 500 | 11 | 500
-1.33 | 40%CO2+60%Xe | 43.71 | 281.82 | 6216.14 | 0.25 | 9.31 | 425 | 10.71 | 525
100%Xe
Table 22. Increasing sCO2-Xe power cycle efficiency by adding CO
Ambient Temperature (ºC) | Working Fluid | Cycle Efficiency (%) | CIT (K) | CIP (kPa) | Recomp. Fraction | HT Pinch Point (K) | HT UA (kW/K) | LT Pinch Point (K) | LT UA (kW/K)
20.98 | 100%CO2 | 42.9 | 304.13 | 7474.89 | 0.31 | 10.17 | 900 | 11.2 | 700
-283.15 | 90%CO2+5%Xe+5%Ar
-283.15 | 80%CO2+10%Xe+10%Ar
-283.15 | 70%CO2+10%Xe+20%Ar
-283.15 | 60%CO2+10%Xe+30%Ar
-283.15 | 50%CO2+10%Xe+40%Ar
-283.15 | 40%CO2+10%Xe+50%Ar
-283.15 | 30%CO2+10%Xe+60%Ar
-283.15 | 20%CO2+10%Xe+70%Ar
-283.15 | 10%CO2+10%Xe+80%Ar
-106.78 | 10%Xe+90%Ar | 57.98 | 176.37 | 7626.91 | 0.22 | 10.01 | 450 | 10.58 | 450
-132.47 | 100%Ar | 62.34 | 150.68 | 4963 | 0.22 | 10.87 | 250 | 9.98 | 275
15.26 | 90%CO2+10%Xe | 43.55 | 298.41 | 7977.87 | 0.25 | 10.11 | 850 | 10.36 | 650
9.51 | 80%CO2+20%Xe | 43.7 | 292.66 | 7168.4 | 0.25 | 10.16 | 725 | 9.55 | 600
4.6 | 70%CO2+30%Xe | 44.71 | 287.75 | 6816.4 | 0.28 | 10.28 | 650 | 9.91 | 700
1 | 60%CO2+40%Xe | 44.99 | 284.15 | 6513.52 | 0.28 | 10.45 | 550 | 9.72 | 700
-0.98 | 50%CO2+50%Xe | 44.17 | 282.17 | 6313.89 | 0.25 | 9.11 | 500 | 11 | 500
-1.33 | 40%CO2+60%Xe | 43.71 | 281.82 | 6216.14 | 0.25 | 9.31 | 425 | 10.71 | 525
100%Xe
|  |  | Tcr | Pcr | Dcr
|  | CO2 | 304.13 | 7377.3 | 467.6
|  | NF3 | 234 | 4460.7 | 562.47
|  | CF4 | 227.51 | 3750 | 625.7
|  | Kr | 209.48 | 5525 | 909.21
|  | CH4 | 190.56 | 4599.2 | 162.66
|  | Ar | 150687 | 4863 | 535.59
|  | CO | 132.86 | 3494 | 303.9
|  | N2 | 126192 | 3395.8 | 313.29
|  | F2 | 144414 | 5172.4 | 592.86
|  | Xe | 289733 | 5842 | 1102.86
|  | Ne | 44.4 | 2661.63 | 486.31

## 100%Kr
63.67

## TurboFan Paper Data Input
The 8th International Supercritical CO2 Power Cycles Symposium February 27 – 29, 2024, San Antonio, Texas Paper #22 sCO2 Waste Heat Recovery System for Turbofan Engine – System Optimization and Component Design
The study is done, and the cycle are analyzed under steady-state cruise operating condition at case 10.
| TIP | 25000 | kPa
| TIT | 722.45 | K
| TOT | 602.85 | K
| Turb. Effic. | 0.9
| CIP | 8470 | kPa
| CIT | 306.05 | K
| COT | 337.15 | K
| Comp. Effic. | 0.75
| RCIT | 356.35 | K
| RCOT | 469.05 | K
| Recomp.Effic. | 0.75